## Operating Data (m3hr-bar)
|  | Reverse Osmosis and Nanofiltration Operating Data Normalization | [6 empty] | Abpaksazan technical and engineering company | [6 empty] | Reverse Osmosis and Nanofiltration Operating Data Normalization | [6 empty] | Abpaksazan technical and engineering company | [6 empty] | Reverse Osmosis and Nanofiltration Operating Data Normalization | [6 empty] | Abpaksazan technical and engineering company | [5 empty] | Reverse Osmosis and Nanofiltration Operating Data Normalization
Plant Identification: |  | Test Train Data |  |  |  |  | Plant Identification: |  | Test Train Data |  |  |  |  | Plant Identification: |  | Test Train Data |  |  |  |  | Plant Identification: |  | Test Train Data |  |  |  |  | Plant Identification: |  | Test Train Data |  |  |  |  | Plant Identification: |  | Test Train Data |  |  |  | Plant Identification: |  | Test Train Data
Start-Up Date: |  | 2019-11-12
Date | 1st Stage Permeate Flow | 2nd Stage Permeate Flow | Total Permeate Flow | 2nd Stage Concentrate Flow | Feed Pressure | 1st Stage Concentrate Pressure | 2nd Stage Concentrate Pressure | 1st Stage Permeate Pressure | 2nd Stage Permeate Pressure | Calculated Feed TDS | Feed Conductivity | Feed TDS | 1st Stage Calc Perm TDS | 1st Stage Permeate Conductivity | 1st Stage Permeate TDS | 2nd Stg Calc Perm TDS | 2nd Stage Permeate Conductivity | 2nd Stage Permeate TDS | Calculated Temp (C) | Feed Temp (F) | Feed Temp (C) | Feed Flow | Days of Operation | System Recovery (%) | 1st Stage Differential Pressure | 2nd Stage Differential Pressure | Temperature Correction Factor | 1st Stage Calculated Feed/Brine Avg Conc | 2nd Stage Calculated Feed/Brine Avg Conc | 2nd Stage Feed Conc | 1st Stage Feed/Brine Osmotic Pressure | 2nd Stage Feed/Brine Osmotic Pressure | 1st Stage Permeate Osmotic Pressure | 2nd Stage Permeate Osmotic Pressure | 1st Stage Net Driving Pressure | 2nd Stage Net Driving Pressure | 1st Stage Normalized Permeate Flow | 2nd Stage Normalized Permeate Flow | System Normalized Permeate Flow | 1st Stage Normalized Permeate Salt Passage | 2nd Stage Normalized Permeate Salt Passage | 1st Stage Normalized Permeate Salt Rejection | 2nd Stage Normalized Permeate Salt Rejection
2007-11-15 | 15 | 7.7 | 22.7 | 7.6 | 9.9 | 8.1 | 6.8 | 0 | 0 | 365.5865 | 750 |  | 0.99405 | 2 |  | 1.9459 | 4 |  | 26.6667 | 80 |  | 30.3 |  | 74.92% | 1.8 | 1.3 | 1.0505 | 504.6029 | 1005.2448 | 723.0302 | 0.4019 | 0.80105 | 0.00079133 | 0.001549 | 8.5989 | 6.6505 | 15 | 7.7 | 22.7 | 0.2719% | 0.2691% | 99.73% | 99.73%
2007-11-17 | 14.7 | 8 | 22.7 | 7.6 | 10 | 8 | 6.9 | 0 | 0 | 378.1231 | 775 |  | 1.4715 | 3 |  | 2.4182 | 5 |  | 26.1111 | 79 |  | 30.3 |  | 74.92% | 2 | 1.1 | 1.0334 | 517.4233 | 1027.9408 | 733.0448 | 0.41135 | 0.81763 | 0.0011693 | 0.0019215 | 8.5898 | 6.6343 | 14.9581 | 8.1517 | 23.1098 | 0.391% | 0.3454% | 99.61% | 99.65%
2007-12-05 | 14.7 | 8 | 22.7 | 7.6 | 10.5 | 8 | 6.9 | 0 | 0 | 353.066 | 725 |  | 1.2333 | 2.5 |  | 2.1822 | 4.5 |  | 25.5556 | 78 |  | 30.3 |  | 74.92% | 2.5 | 1.1 | 1.0166 | 483.1352 | 960.0082 | 684.6007 | 0.38337 | 0.76213 | 0.00097816 | 0.0017307 | 8.8676 | 6.6896 | 14.7292 | 8.2181 | 22.9472 | 0.3568% | 0.3393% | 99.64% | 99.66%
2007-12-15 | 15 | 7.7 | 22.7 | 7.6 | 11.4 | 8.2 | 7 | 0 | 0 | 365.5865 | 750 |  | 1.4715 | 3 |  | 2.4182 | 5 |  | 24.4444 | 76 |  | 30.3 |  | 74.92% | 3.2 | 1.2 | 0.98361 | 504.6029 | 1004.594 | 722.562 | 0.39892 | 0.79459 | 0.0011628 | 0.0019108 | 9.4022 | 6.8073 | 14.6507 | 8.0339 | 22.6846 | 0.4299% | 0.3574% | 99.57% | 99.64%
2008-01-05 | 14 | 8.7 | 22.7 | 7.6 | 11.6 | 8.5 | 7.2 | 0 | 0 | 378.1231 | 775 |  | 1.9459 | 4 |  | 2.6538 | 5.5 |  | 25 | 77 |  | 30.3 |  | 74.92% | 3.1 | 1.3 | 1 | 507.373 | 1002.4365 | 701.2201 | 0.40186 | 0.79436 | 0.0015404 | 0.0021009 | 9.6497 | 7.0577 | 13.1049 | 8.6116 | 21.7166 | 0.519% | 0.4368% | 99.48% | 99.56%
Note on C6: Enter the reverse osmosis or nanofiltration plant identification. Enter train ID if more than one train.
Note on C8: Enter the start-up date for the unit or train. Use the format shown in this example: 04-Nov-2007.
Note on A10: The date should be entered using the following format: dd-mmm-yyyy (e.g., 04-Nov-1999).
Note on D10: This is the sum of the first and second stage permeate flow rates
Note on L10: Enter Feed Conductivity if the concentrations are measured using a conductivity meter.
Note on M10: Enter Feed Concentration as total dissolved solids (TDS) if concentration is measured as TDS.
Note on O10: Enter Permeate Conductivity if the concentrations are measured using a conductivity meter.
Note on P10: Enter Permeate Concentration as total dissolved solids (TDS) if concentration is measured as TDS.
Note on R10: Enter Permeate Conductivity if the concentrations are measured using a conductivity meter.
Note on S10: Enter Permeate Concentration as total dissolved solids (TDS) if concentration is measured as TDS.
Note on U10: When the feed temperature is entered as degrees F, it will be recalculated as degrees C
Note on W10: The feed flow to the membrane system is calculated.
Note on X10: The number of days the unit has been in operation with these elements is calculated here
Note on Y10: The system recovery, expressed as a percentage, is calculated here.
Note on Z10: The differential pressure across the 1st stage is calculated here.
Note on AA10: The differential pressure across the 2nd stage is calculated here.
Note on AB10: The temperature correction factor, TCF, is calculated here.
Note on AC10: The 1st stage actual feed/concentrate average concentration is calculated here for estimating the permeate osmotic pressure.
Note on AD10: The 2nd stage actual feed/concentrate average concentration is calculated here for estimating the permeate osmotic pressure.
Note on AE10: The feed concentration to the 2nd stage elements is calculated here.
Note on AF10: The 1st stage actual feed/brine osmotic pressure is calculated here using the feed/brine concentration.
Note on AG10: The 2nd stage actual feed/brine osmotic pressure is calculated here using the feed/brine concentration.
Note on AH10: The 1st stage actual permeate osmotic pressure is calculated here using the permeate concentration.
Note on AI10: The 2nd stage actual permeate osmotic pressure is calculated here using the permeate concentration.
Note on AJ10: The 1st stage actual net driving pressure (NDPa) is calculated here.
Note on AK10: The 2nd stage actual net driving pressure (NDPa) is calculated here.
Note on AL10: The 1st stage normalized permeate flow is calculated from measured flow which is adjusted to conditions at startup.
Note on AM10: The 2nd stage normalized permeate flow is calculated from measured flow which is adjusted to conditions at startup.
Note on AO10: 1st stage normalized permeate salt passage is calculated here.
Note on AP10: 2nd stage normalized permeate salt passage is calculated here.
Note on AQ10: 1st stage normalized permeate salt rejection is calculated here.
Note on AR10: 2nd stage normalized permeate salt rejection is calculated here.

## Conductivity to TDS (hidden)
| a | b | c
> 7630 | 8.0091e-11 | -50.6458 | 112.484
<= 7630 | 7.7014e-20 | -90.4756 | 188.8844